## Introduction to GWR
Do you want to show you have 4 log inactivation?
It really depends on your water system as whether it is to your advantage to show you have 4 log inactivation.
Pros (If you do show 4 log inactivation)-
You do not have to take "triggered" samples after each positive TCR sample.
Cons (if you do show 4 log inactivation)-
Systems < 3300 people
You must perform daily grab chlorine monitoring everyday at each site after treatment during the
hour of peak flow which is at or prior to the first customer and calculate your CT each day.
Systems >= 3300 people
You must continuously monitor/maintain the proper chlorine residual and calculate your CT daily.
Considerations-
Number of groundwater sources you have as each must be monitored after a positive TCR sample
Number of positive TCR samples you have each year as this triggers source monitoring
Cost of triggered samples-lab fees, postage, labor, etc.
Cost to take daily chlorine residuals
Cost to calculate CT each day
Cost to install chlorination equipment if you currently do not chlorinate
Cost to install chlorine monitoring equipment if your system is serves more than 3300 people
Cost to install source water monitoring taps if none are present
…so if you have a single TCR positive sample every four years and you have only one well, it might be more
economical NOT to show you have 4 log inactivation and take the triggered sample when it is required.
One triggered sample every four years--> $20 (estimated lab cost only) per 4 years

## Instructions to Use Spreadsheet
Instructions to Use This Spreadsheet---Version-November 18, 2009
The worksheet entitled "GWRCTCalculation" calculates your CT at any one time.
Rows 1-17 show the actual CT values that must be obtained by your system to be in compliance.
Rows 18-29 summarize your work from the lower portion of spreadsheet and determine your compliance.
Rows 30-85 are where you calculate the CT for your system.
Rows 86-98 show the Baffling Factors for a reservoir.
Start with Cell B27. This is where you indicate the CT that your system must obtain.
Using the column with the temperature for your water, find the CT value necessary for 4 log inactivation and
indicate this value in Cell B27. This is the CT value that your system must obtain to be in compliance.
In Cell N20, use the "drop down box" to indicate the type of disinfectant that your system uses.
In Cell Q20, use the "drop down box" to indicate the type of disinfectant sampling that your system uses.
Next, determine which features of your water system will contribute to the CT. This includes any structure
where water can reside between the disinfectant point and where the disinfectant level will be measured at or
prior to the first customer. These features can be pipe, clearwells/reservoirs of any shape, etc. You will use
only the portions of the worksheet that apply to your system, i.e. pipes, cylindrical reservoirs, or rectangular
reservoirs.
PIPE-You will most likely have pipe between your disinfectant point and the point of disinfectant measurement.
Indicate the diameter of the pipe in INCHES in Cell J32. Indicate the length of pipe in FEET in Cell J35. You can
have several sections of pipe. As long as they are the same diameter, you add the lengths together. (If you have
pipe of different diameter, you need to make changes to this spreadsheet to be able to use the pipe section
more than once.) Indicate the highest flow for the day in GPM in Cell J38. Indicate the disinfectant measurement
in MILLIGRAMS PER LITER in Cell J41. (Note-You must take your disinfectant measurement at the time of the
highest daily flow.)
CYLINDRICAL RESERVOIR-If you have a cylindrical reservoir or clearwell between the disinfectant point and
the point of disinfectant measurement, you will use this section. Indicate the diameter of the reservoir in FEET
in Cell J50. Indicate the MINIMUM HEIGHT of water for the day in the reservoir in FEET in Cell J53. Indicate
the Baffling Factor from the chart in Cell J59. The highest daily flow and the disinfectant level will already be
indicated based on your information that you provided with the pipe CT determination.
RECTANGULAR RESERVOIR-If you have a rectangular reservoir or clearwell between the disinfectant point and
the point of disinfectant measurement, you will use this section. Indicate the length of the reservoir in Feet
in Cell K71 and the width in FEET in Cell M71. Indicate the MINIMUM HEIGHT of water for the day in the
reservoir in FEET in Cell J74. Indicate the Baffling Factor from the chart in Cell J80. The highest daily flow and
the disinfectant level will already be indicated based on your information that you provided with the pipe CT
determination.
The total CT for your entire system will now appear in Cell K20 and the determination of whether you are in
compliance with your required CT will appear in Cell E27. PLEASE REALIZE THAT THIS IS YOUR COMP-
LIANCE FOR A SINGLE DAY. You only have to complete this section of spreadsheet once to be able to use
the "Monthly Summmary" worksheet.
Compliance for a Month
To track your compliance for a particular month to submit to DENR, you must use the worksheet entitled
"Monthly Summary".
Start with Cell C3 for your system's name, Cell C4 for the system's EPA ID number, Cell C5 for the month
and year, and Cell I5 for population. Cell C6 (your system's required CT value), Cell I3 (disinfectant type), and
Cell I4 (Sampling Type) have already been completed based on the instructions above for the
GWRCTCalculation worksheet.
Again you will only use the sections of the Monthly Summary that pertain to the features of your system, i.e.
Pipe CT, Cylindrical Reservoir CT, or Rectangular Reservoir CT.
PIPE CT-Column B (Pipe Volume) has already been calculated based on your previous work. Use Column C
for the daily highest flow in GPM and Column D for the daily disinfectant measurement in MILLIGRAMS PER
LITER. Column E calculates the CT for the pipe portion of your system.
CYLINDRICAL RESERVOIR CT-Column G has the cross sectional area of the reservoir that was calculated on
"GWRCTCalculation" worksheet. Use Column H for the minimum reservoir height for the day. Column I (Flow)
and Column K (Residual) are already completed from the Pipe CT from the "Monthly Summary" worksheet
while Column J (Baffling Factor) was already completed from the "GWRCTCalculation" worksheet. Column L
calculates the CT for the cylindrical reservoir portion of your system.
RECTANGULAR RESERVOIR CT-Column N has the cross sectional area of the reservoir that was calculated on
"GWRCTCalculation" worksheet. Use Column O for the minimum reservoir height for the day. Column P (Flow)
and Column R (Residual) are already completed from the Pipe CT from the "Monthly Summary" worksheet
while Column Q (Baffling Factor) was already completed from the "GWRCTCalculation" worksheet. Column S
calculates the CT for the rectangular reservoir portion of your system.
TOTAL DAILY CT-Column U will then calculate the total CT for your system while Column V will determine
if your system is in compliance.
This monthly compliance worksheet should be printed and submitted to DENR each month to show that your
system is maintaining a 4 log inactivation.

## GWRCTCalculation
Calculating "CT" for Groundwater Rule Compliance
Free Chlorine
CT = C x T | [20 empty] | Chlorine Dioxide
C = Concentration of disinfectant residual (mg/L) measured at a point at or before 1st customer | [20 empty] | Ozone
T = contact time (minutes) between point of disinfectant application and point where residual is measured | [20 empty] | Chloramines
CT is expressed as mg-min/L
0.1
0.3
CT Values for Inactivation of Viruses by Free Chlorine-pH 6.0-9.0 | [20 empty] | 0.5
Degrees-C | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 0.7
Degrees-F | 33.8 | 35.6 | 37.4 | 39.2 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 60.8 | 62.6 | 64.4 | 66.2 | 68 | 1
Inactivation (log)
2 | 5.8 | 5.3 | 4.9 | 4.4 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3 | 2.8 | 2.6 | 2.4 | 2.2 | 2 | 1.8 | 1.6 | 1.4 | 1.2 | 1 | Continuous
3 | 8.7 | 8 | 7.3 | 6.7 | 6 | 5.6 | 5.2 | 4.8 | 4.4 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3 | 2.8 | 2.6 | 2.4 | 2.2 | 2 | Grab
4 | 11.6 | 10.7 | 9.8 | 8.9 | 8 | 7.6 | 7.2 | 6.8 | 6.4 | 6 | 5.6 | 5.2 | 4.8 | 4.4 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3
CT for Pipe |  | Plus | CT for Cylindrical Reservoir |  | Plus | CT for Rectangular Reservoir |  | Equals | Total CT for System* |  |  | Disinfectant Type |  |  | Disinfectant Sampling Type
0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | Free Chlorine |  |  | Continuous
|  |  | (if applicable) |  |  | (if applicable)
*Compare your CT calculation with chart above for 4 log inactivation for your water temperature. If your CT exceeds
value on chart, you are achieving a 4 log inactivation and are in compliance.
Your Required CT Value* |  |  | Compliance?*
Out of Compliance
Basic Formulas for a Pipe
-Calculating Pipe Cross Sectional Area (FT2) | [7 empty] | Pipe Diameter (Inches) |  |  |  | 0 |  |  | ft2
| ¶ R 2 | [6 empty] | 0
-Calculating Pipe Volume (gallons) | [7 empty] | Pipe Length (Feet) |  |  |  | 0 |  |  | gallons
| pipe length x cross sectional area | [6 empty] | 0
-Calculating Disinfectant Contact Time (minutes) | [7 empty] | Highest Flow Rate (gpm)** |  |  |  | 0 |  |  | minutes
| pipe volume / flow | [6 empty] | 1
-Calculating CT (mg-min/L or CT) for this pipe | [7 empty] | Lowest Residual (mg/L) |  |  |  | 0 |  |  | CT
| disinfectant residual x contact time | [6 empty] | 0
**This is the maximum flow for the day
Basic Formulas for a Cylidrical Reservoir
-Calculating Reservoir Cross Sectional Area (FT2) | [7 empty] | Reservoir Diameter (Feet) |  |  |  | 0 |  |  | ft2
| ¶ R 2 | [6 empty] | 0
-Calculating Volume of Water in Reservoir (gallons) | [7 empty] | Minimum Height of Water (Feet)*** |  |  |  | 0 |  |  | gallons
| water height x cross sectional area | [6 empty] | 0
-Calculating Disinfectant Contact Time (minutes) | [7 empty] | Highest Flow Rate (gpm)** |  |  |  | 0 |  |  | minutes
| reservoir volume / flow | [6 empty] | 1
-Baffling Factor**** | [7 empty] | Baffling Factor |  |  |  | 0 |  |  | effective minutes
-Calculating CT (mg-min/L or CT) for this pipe | [7 empty] | Lowest Residual (mg/L) |  |  |  | 0 |  |  | CT
| disinfectant residual x contact time | [6 empty] | 0
***This is the minimum height of water in the reservoir for the day.
Basic Formulas for a Rectangular Reservoir
-Calculating Cross Sectional Area (FT2) | [7 empty] | Reservoir Dimensions (Feet) |  |  |  | 0 |  |  | ft2
| length x width | [6 empty] | Length | 0 | Width | 0
-Calculating Volume of Water in Reservoir (gallons) | [7 empty] | Minimum Height of Water (Feet)*** |  |  |  | 0 |  |  | gallons
| water height x cross sectional area | [6 empty] | 0
-Calculating Disinfectant Contact Time (minutes) | [7 empty] | Highest Flow Rate (gpm)** |  |  |  | 0 |  |  | minutes
| reservoir volume / flow | [6 empty] | 1
-Baffling Factor**** | [7 empty] | Baffling Factor |  |  |  | 0 |  |  | effective minutes
-Calculating CT (mg-min/L or CT) for this reservoir | [7 empty] | Lowest Residual (mg/L) |  |  |  | 0 |  |  | CT
| disinfectant residual x contact time | [6 empty] | 0
****Baffling Factors
| Unbaffled | 0.1 | None
| Poor | 0.3 | Single or multiple unbaffled inlets/outlets, no intra-basin baffles
| Average | 0.5 | Baffled inlet OR outlet w/ some intra-basin baffles
| Superior | 0.7 | Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated launders
| Perfect | 1.0 | Very high length to width ratio (pipeline flow), perforated inlet, outlet, and intra-basin baffles
Based on spreadsheet from Kansas Dept of Health & Environment

## Example Calculation
Calculating "CT" for Groundwater Rule Compliance-EXAMPLE
Free Chlorine
Your system uses free chlorine to disinfect the water. The water temperature for the day is 46.4 degrees F and the pH is 8.0. | [20 empty] | Ozone
You have one well and chlorinate at the well. From that point, there is a 6" water line that runs 200 ' to a cylindrical clearwell that is | [20 empty] | Chlorine Dioxide
40' in diameter. The maximum usable depth is 25'; however, on this day the minimum height of the water is 20'. After the water exits | [20 empty] | Chloramines
the clearwell, it flows thru another 6" pipe approximately 200' to a sampling station where the free chlorine residual is measured.
The maximum flow rate for the day is 200 gpm. The lowest measured residual is 0.5 mg/l. The clearwell has no baffling. | [20 empty] | 0.1
0.3
0.5
0.7
CT Values for Inactivation of Viruses by Free Chlorine-pH 6.0-9.0 | [20 empty] | 1
Degrees-C | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Degrees-F | 33.8 | 35.6 | 37.4 | 39.2 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 60.8 | 62.6 | 64.4 | 66.2 | 68
Inactivation (log)
2 | 5.8 | 5.3 | 4.9 | 4.4 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3 | 2.8 | 2.6 | 2.4 | 2.2 | 2 | 1.8 | 1.6 | 1.4 | 1.2 | 1
3 | 8.7 | 8 | 7.3 | 6.7 | 6 | 5.6 | 5.2 | 4.8 | 4.4 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3 | 2.8 | 2.6 | 2.4 | 2.2 | 2
4 | 11.6 | 10.7 | 9.8 | 8.9 | 8 | 7.6 | 7.2 | 6.8 | 6.4 | 6 | 5.6 | 5.2 | 4.8 | 4.4 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3
CT for Pipe |  | Plus | CT for Cylindrical Reservoir |  | Plus | CT for Rectangular Reservoir |  | Equals | Total CT for System* |  |  | Disinfectant Type
1.468 |  |  | 469.744 |  |  | 0 |  |  | 471.212 |  |  | Free Chlorine
|  |  | (if applicable) |  |  | (if applicable)
*Compare your CT calculation with chart above for 4 log inactivation for your water temperature. If your CT exceeds
value on chart, you are achieving a 4 log inactivation and are in compliance.
Your Required CT Value* |  |  | Compliance?*
6.8 |  |  | In Compliance
In this example, you have a total of 400' of 6" pipe that has a CT of 1.5. You also have a CT in the reservoir of 469.7 for a
total CT of 471.2 for the pipe and reservoir. You are required to have a CT of 6.8 (obtained from above chart). Your CT of
471.2 exceeds 6.8 so you are in compliance for this day.
Basic Formulas for a Pipe
-Calculating Pipe Cross Sectional Area (FT2) | [7 empty] | Pipe Diameter (Inches) |  |  |  | 0.19625 |  |  | ft2
| ¶ R 2 | [6 empty] | 6
-Calculating Pipe Volume (gallons) | [7 empty] | Pipe Length (Feet) |  |  |  | 587.18 |  |  | gallons
| pipe length x cross sectional area | [6 empty] | 400
-Calculating Disinfectant Contact Time (minutes) | [7 empty] | Highest Flow Rate (gpm)** |  |  |  | 2.9359 |  |  | minutes
| pipe volume / flow | [6 empty] | 200
-Calculating CT (mg-min/L or CT) for this pipe | [7 empty] | Lowest Residual (mg/L) |  |  |  | 1.468 |  |  | CT
| disinfectant residual x contact time | [6 empty] | 0.5
**This is the maximum flow for the day
Basic Formulas for a Cylidrical Reservoir
-Calculating Reservoir Cross Sectional Area (FT2) | [7 empty] | Reservoir Diameter (Feet) |  |  |  | 1256 |  |  | ft2
| ¶ R 2 | [6 empty] | 40
-Calculating Volume of Water in Reservoir (gallons) | [7 empty] | Minimum Height of Water (Feet)*** |  |  |  | 187897.6 |  |  | gallons
| water height x cross sectional area | [6 empty] | 20
-Calculating Disinfectant Contact Time (minutes) | [7 empty] | Highest Flow Rate (gpm)** |  |  |  | 939.488 |  |  | minutes
| reservoir volume / flow | [6 empty] | 200
-Baffling Factor**** | [7 empty] | Baffling Factor |  |  |  | 93.9488 |  |  | effective minutes
0.1
-Calculating CT (mg-min/L or CT) for this pipe | [7 empty] | Lowest Residual (mg/L) |  |  |  | 469.744 |  |  | CT
| disinfectant residual x contact time | [6 empty] | 0.5
***This is the minimum height of water in the reservoir for the day.
Basic Formulas for a Rectangular Reservoir
-Calculating Cross Sectional Area (FT2) | [7 empty] | Reservoir Dimensions (Feet) |  |  |  | 0 |  |  | ft2
| length x width | [6 empty] | Length | 0 | Width | 0
-Calculating Volume of Water in Reservoir (gallons) | [7 empty] | Minimum Height of Water (Feet)*** |  |  |  | 0 |  |  | gallons
| water height x cross sectional area | [6 empty] | 0
-Calculating Disinfectant Contact Time (minutes) | [7 empty] | Highest Flow Rate (gpm)** |  |  |  | 0 |  |  | minutes
| reservoir volume / flow | [6 empty] | 200
-Baffling Factor**** | [7 empty] | Baffling Factor |  |  |  | 0 |  |  | effective minutes
0
-Calculating CT (mg-min/L or CT) for this reservoir | [7 empty] | Lowest Residual (mg/L) |  |  |  | 0 |  |  | CT
| disinfectant residual x contact time | [6 empty] | 0.5
****Baffling Factors
| Unbaffled | 0.1 | None
| Poor | 0.3 | Single or multiple unbaffled inlets/outlets, no intra-basin baffles
| Average | 0.5 | Baffled inlet OR outlet w/ some intra-basin baffles
| Superior | 0.7 | Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated launders
| Perfect | 1.0 | Very high length to width ratio (pipeline flow), perforated inlet, outlet, and intra-basin baffles
Based on spreadsheet from Kansas Dept of Health & Environment

## Monthly Summary
Monthly Summary of GWR CT Values
System Name- |  |  |  |  | Disinfectant Type- |  | Free Chlorine
EPA ID#- |  |  |  |  | Sampling Type- |  | Continuous
Month/Yr- |  |  |  |  | Population-
Required CT Value-
| Pipe CT |  |  |  | Cylindrical Reservoir CT | [5 empty] | Rectangular Reservoir CT
Date | Pipe Volume | Max Daily Flow | Residual | Pipe CT | Cross Section Area | Min Water Ht | Max Daily Flow | Baffling Factor | Residual | Reser-voir CT | Cross Section Area | Min Water Ht | Max Daily Flow | Baffling Factor | Residual | Reser-voir CT | Required Daily CT | Total Daily CT | Compliance?
1 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
2 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
3 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
4 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
5 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
6 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
7 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
8 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
9 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
10 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
11 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
12 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
13 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
14 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
15 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
16 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
17 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
18 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
19 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
20 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
21 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
22 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
23 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
24 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
25 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
26 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
27 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
28 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
29 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
30 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!
31 | 0 |  |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! | 0 |  |  | 0 |  | #VALUE! |  | #VALUE! | #VALUE!

## Other CT Values
CT Values for Inactivation of Viruses by Chlorine Dioxide-pH 6.0-9.0
Temp C | <=1 | 5 | 10 | 15 | 20 | 25
2-log | 8.4 | 5.6 | 4.2 | 2.8 | 2.1 | 1.4
3-log | 25.6 | 17.1 | 12.8 | 8.6 | 6.4 | 4.3
4-log | 50.1 | 33.4 | 25.1 | 16.7 | 12.5 | 8.4
CT Values for Inactivation of Viruses by Ozone
Temp C | <=1 | 5 | 10 | 15 | 20 | 25
2-log | 0.9 | 0.6 | 0.5 | 0.3 | 0.25 | 0.15
3-log | 1.4 | 0.9 | 0.8 | 0.5 | 0.4 | 0.25
4-log | 1.8 | 1.2 | 1 | 0.6 | 0.5 | 0.3
CT Values for Inactivation of Viruses by Chloramine
Temp C | <=1 | 5 | 10 | 15 | 20 | 25
2-log | 1243 | 857 | 643 | 428 | 321 | 214
3-log | 2063 | 1423 | 1067 | 712 | 534 | 356
4-log | 2883 | 1988 | 1491 | 994 | 746 | 497